## 90.1 2007 Exterior
90.1-2007 - Whole Building Method - Exterior |  |  | Calculation Date: | 2014-03-31
Tradable Surfaces
Uncovered Parking Areas |  | Per Unit Allowance | Allowance
| Area | VA/Ft2 | VA
Parking Lots | 0 | 0.15 | 0
Building Grounds
| Linear Ft | VA/Ft
Walkways < 10' Wide | 0 | 1 | 0
| Area | VA/Ft2
Walkways > 10' Wide | 0 | 0.2 | 0
Plaza Areas | 0 | 0.2 | 0
| Area | VA/Ft2
Stairways | 0 | 1 | 0
Building Entrances / Exits
| Linear Ft | VA/Ft
Main Entries | 0 | 30 | 0
Other Doors | 0 | 20 | 0
Canopies and Overhangs
| Area | VA/Ft2
Canopies | 0 | 1.25 | 0
Outdoor Sales
| Area | VA/Ft2
Open Areas | 0 | 0.5 | 0
| Linear Ft | VA/Ft
Street Frontage | 0 | 20 | 0
|  | ASHRAE ALLOWANCE | 0
|  | LEED ALLOWANCE | 0
Exterior Fixtures
Type | Quantity | VA / Fixture | Total VA | Per Fixture / LED ALT | Assembly | Total Lumens | % Up | 90-180 Lumens
| 0 | 76 | 0 | 0 | 1 | 0 | 0 | 0
|  | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Total | 0 | Total Lumens |  | 0
|  |  |  | 2% |  | 0 |  | 0

## 90.1 2007 Interior
90.1-2007 - Whole Building Method - Interior |  |  | Calculation Date: | 2014-03-31
Building FT2: | 0 |  |  |  | Total Allowed VA: | 0 | LEED 14% | 0
VA/FT2: | 1 |  |  |  | Total Connected VA: | 0 | LEED 21% | 0
[5 empty] | Over (Red) / Under (Green) : | 0 | Current Savings: | #DIV/0!
[5 empty] | VA/ FT2: | #DIV/0!
Fixture Types: | Quantity | VA / Fixture Type | Total
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | Total | 0
Theatrical Lighting
T(12)T(16)T(20 | (4)(1)(1) | N/A
TA | 0 | 100
TB | 1 | 100
TC | 0 | 100
TD | 0 | 250
TE | 0 | 250
TF | 0 | 71

## ASHRAE Space
90.1-2004 - Space-by-Space Method - Interior
Space Type | 1st Floor Ft2 |  |  | Allowed VA/Ft2 | Total VA
Electrical / Mechanical | 1 | 0 | 0 | 1.5 | 1.5
Lobby | 1 | 0 | 0 | 1.3 | 1.3
Restrooms | 1 | 0 | 0 | 0.9 | 0.9
Stairs | 1 | 0 | 0 | 0.6 | 0.6
Corridor | 1 | 0 | 0 | 0.5 | 0.5
Food Preparation | 1 | 0 | 0 | 1.2 | 1.2
Multi-Purpose | 1 | 0 | 0 | 1.3 | 1.3
Office | 1 | 0 | 0 | 1.1 | 1.1
Conference / Convention | 1 | 0 | 0 | 1.3 | 1.3
Storage / Janitor | 1 | 0 | 0 | 0.8 | 0.8
Garage | 1 | 0 | 0 | 0.2 | 0.2
Gymnasium | 1 | 0 | 0 | 1.4 | 1.4
Natatorium | 1 | 0 | 0 | 1.4 | 1.4
Exercise Area | 1 | 0 | 0 | 0.9 | 0.9
Locker / Dressing | 1 | 0 | 0 | 0.6 | 0.6
Theater | 1 | 0 | 0 | 2.6 | 2.6
Laundry | 1 | 0 | 0 | 0.6 | 0.6
Lounge | 1 | 0 | 0 | 1.2 | 1.2
Nursery | 1 | 0 | 0 | 0.6 | 0.6
Classrooms | 1 | 0 | 0 | 1.4 | 1.4
Workshop | 1 | 0 | 0 | 1.9 | 1.9
Dining | 1 | 0 | 0 | 0.9 | 0.9
Total Ft2 | 22 | 0 | 0 | Total Allowed VA | 24.2
|  |  |  | Total Ft2 | 22
|  |  |  | Allowed Total VA/Ft2 | 1.1
90.1-2004 - Additional Interior Lighting Power
Area | Area Ft2 | Fixture Types |  | Allowed VA/Ft2 | Total VA | Used VA
x | 1 | x |  | 1 | 1 | 1
x | 1 | x |  | 1 | 1 | 1
x | 1 | x |  | 1 | 1 | 1
x | 1 | x |  | 1 | 1 | 1
x | 1 | x |  | 1 | 1 | 1
x | 1 | x |  | 1 | 1 | 1
x | 1 | x |  | 1 | 1 | 1
Connected Lighting
Total VA | 0
Ft2 | 0
Total VA/Ft2 | #DIV/0!
Classrooms | Area |  | Offices | Area |  | Exercise Area | Area
Total | 0
Corridors | Area |  |  |  |  | Lounge | Area
[6 empty] | Total | 0
[6 empty] | Locker / Dressing | Area
Total | 0
[6 empty] | Total | 0
Multi-Purpose | Area |  | Total | 0
|  |  | Workshop | Area |  | Dining | Area
|  |  | 108 | 931
Theater | Area |  | Conference | Area
|  |  | 116 | 4909 |  | Food Preparation | Area
|  |  | 121 | 385
Total | 1 |  | 110 | 171
|  |  | Total | 5465 |  | Total | 0
Storage | Area
[6 empty] | Nursery | Area
|  |  | Restrooms | Area
[6 empty] | Total | 0
[6 empty] | Stair | Area
[6 empty] | Lobby | Area
|  |  | Total | 0
|  |  | Elect / Mech / AV | Area |  | Total | 0
[6 empty] | Laundry | Area
Total | 0
|  |  | Total | 0

## Voltage Drop
Series 1P Voltage Drop |  |  | 1P (2) or 3P (1): | 2
Note: Assume Balanced Load for 3P
Fixture # | Distance | Total Dist - Fixture | VA | Total VA | Voltage | VD | % VD | K | CM
1 | 2 | 2 | 7.5 | 67.5 | 12 | 0.027204 | 0.2267 | 12.55 | 10380
2 | 12 | 14 | 7.5 | 60 | 11.9728 | 0.14542 | 1.4385 | 12.55 | 10380
3 | 12 | 26 | 7.5 | 52.5 | 11.8274 | 0.1288 | 2.5119 | 12.55 | 10380
4 | 12 | 38 | 7.5 | 45 | 11.6986 | 0.11162 | 3.442 | 12.55 | 10380
5 | 12 | 50 | 7.5 | 37.5 | 11.587 | 0.093912 | 4.2246 | 12.55 | 10380
6 | 12 | 62 | 7.5 | 30 | 11.493 | 0.075743 | 4.8558 | 12.55 | 10380
7 | 12 | 74 | 7.5 | 22.5 | 11.4173 | 0.057184 | 5.3323 | 12.55 | 10380
8 | 12 | 86 | 7.5 | 15 | 11.3601 | 0.038315 | 5.6516 | 12.55 | 10380
9 | 12 | 98 | 7.5 | 7.5 | 11.3218 | 0.019222 | 5.8118 | 12.55 | 10380
10 | 12 | 110 | 0 | 0 | 11.3026 | 0 | 5.8118 | 12.55 | 10380
11 | 0 | 110 | 0 | 0 | 11.3026 | 0 | 5.8118 | 12.55 | 10380
12 | 0 | 110 | 0 | 0 | 11.3026 | 0 | 5.8118 | 12.55 | 10380
13 | 0 | 110 | 0 | 0 | 11.3026 | 0 | 5.8118 | 12.55 | 10380
14 | 0 | 110 | 0 | 0 | 11.3026 | 0 | 5.8118 | 12.55 | 10380
15 | 0 | 110 | 0 | 0 | 11.3026 | 0 | 5.8118 | 12.55 | 10380
|  | Total VA: | 67.5
3P Voltage Drop |  |  |  | User Data
|  |  |  | AWG | CM | K | Amp 60 | Amp 75
K | 12.87 |  |  | #12 | 6530 | 12.6 | 25
Distance | 150 |  |  | #10 | 10380 | 12.55 | 30
Line Current | 725 |  |  | #8 | 16510 | 12.6 | 40
CM | 33694 |  |  | #6 | 26240 | 12.88 | 55
Voltage | 480 |  |  | #4 | 41740 | 12.85 | 70
|  |  |  | #3 | 52620 | 12.89 | 85
VD | 71.9454 |  |  | #2 | 66360 | 12.87 | 95
% VD | 14.9886 |  |  | #1 | 83690 | 12.88 | 111 | 130
|  |  |  | #1/0 | 105600 | 12.88 |  | 150
|  |  |  | #2/0 | 133100 | 12.87 |  | 175
|  |  |  | #3/0 | 167800 | 12.85 |  | 200
|  |  |  | #4/0 | 211600 | 12.86 |  | 230
|  |  |  | 250 kcmil | 250000 | 12.88 |  | 255
|  |  |  | 500 kcmil | 500000 | 12.9 |  | 380
|  |  |  | 1000 kcmil | 1000000 | 12.9 |  | 545

## Commercial Service
Title | [7 empty] | 15091 | ft^2 Total
H Branch: | [7 empty] | Voltage (3P): | 208
All Floors:
| Load | Units | Mult | Units | Ext | DF | Ext
Lighting | 3.5 | VA/FT^2 | 15091 | ft^2 | 52818.5 | 100% | 52818.5
Receptacles | 1 | VA/FT^2 | 15091 | ft^2 | 10000 | 100% | 10000
|  |  |  | 15091 | 5091 | 50% | 2545.5
Water Heat: | 54000 | W | 1 | ea | 54000 | 100% | 54000
Elevator #1: | 0 | VA | 1 | lump | 0 | 125% | 0
Elevator #2: | 0 | VA | 1 | lump | 0 | 100% | 0
BusDuct: | 0 | VA/FT^2 | 15091 | ft^2 | 0 | 100% | 0
[7 empty] | Total: | 119364 | VA | 331.3311 | A
M Branch:
All Floors:
| Load | Units | Mult | Units | Ext | DF | Ext
Mechanical | 20 | VA/FT^2 | 15091 | ft^2 | 301820 | 100% | 301820
Motors | 4 | VA/FT^2 | 15091 | ft^2 | 60364 | 100% | 60364
Other | 1 | VA/FT^2 | 15091 | ft^2 | 15091 | 100% | 15091
[7 empty] | Total: | 377275 | VA | 1047.2414 | A
Service Totals: | [5 empty] | H Branch | Total: | 119364 | VA | 331.3311 |  | A
[6 empty] | M Branch | Total: | 377275 | VA | 1047.2414 |  | A
[6 empty] | Building | Total: | 496639 | VA | 1378.5725 |  | A
[7 empty] | Total Sq Ft: | 15091 | Sq ft
[7 empty] | VA/ft sq: | 32.9096

## Existing Dwelling Service
Optional Existing Single Dwelling Service Calculation - 220.30
Total Units | 1 |  |  | Demand Notes
Type A Units | 1 | 3500 | 3500
Type B Units | 0 | 0 | 0
Type C Units | 0 | 0 | 0
Type D Units | 0 | 0 | 0
Total Ft2 |  |  | 3500
| Load | Units | Mult | Units | Ext | DF | Total
Lighting | 3 | VA/FT^2 | 3500 | ft^2 | 10500 | 100% | 10500
Small Appliance BC | 1500 | VA | 2 | ea | 3000 | 100% | 3000
Laundry BC | 1500 | VA | 1 | ea | 1500 | 100% | 1500
Range | 8000 | VA | 1 | ea | 8000 | 100% | 8000
Dryer | 5000 | VA | 1 | ea | 5000 | 100% | 5000
Microwave | 1200 | VA | 1 | ea | 1200 | 100% | 1200
Refrigerator | 1200 | VA | 1 | ea | 1200 | 100% | 1200
Disposer | 950 | VA | 1 | ea | 950 | 100% | 950
Dishwasher | 1200 | VA | 1 | ea | 1200 | 100% | 1200
TBD | 0 | VA | 0 | ea | 0 | 100% | 0
TBD | 0 | VA | 0 | ea | 0 | 100% | 0
Water Heater | 4500 | VA | 2 | ea | 9000 | 100% | 9000
[6 empty] | Total VA Without Heat | 41550
Mechanical | 15500 | VA/FT^2 | 1 | ft^2 | 15500 | 100% | 15500
Service Totals:
[6 empty] | First 8KVA @100% | 8000
[6 empty] | Remaining @ 40% | 13420
[6 empty] | HVAC @ 100% | 15500
[6 empty] | Total Demand | 36920
[6 empty] | Amps @ 240V, 1P | 153.8333
[6 empty] | Area Ft2 | 3500
[6 empty] | VA/FT^2 | 10.5486

## Dwelling Service
Optional Single Dwelling Service Calculation - 220.30
Total Units | 1 |  |  | Demand Notes
Type A Units | 1 | 3500 | 3500
Type B Units | 0 | 0 | 0
Type C Units | 0 | 0 | 0
Type D Units | 0 | 0 | 0
Total Ft2 |  |  | 3500
| Load | Units | Mult | Units | Ext | DF | Total
Lighting | 3 | VA/FT^2 | 3500 | ft^2 | 10500 | 100% | 10500
Small Appliance BC | 1500 | VA | 2 | ea | 3000 | 100% | 3000
Laundry BC | 1500 | VA | 1 | ea | 1500 | 100% | 1500
Range | 8000 | VA | 1 | ea | 8000 | 100% | 8000
Dryer | 5000 | VA | 1 | ea | 5000 | 100% | 5000
Microwave | 1200 | VA | 1 | ea | 1200 | 100% | 1200
Refrigerator | 1200 | VA | 1 | ea | 1200 | 100% | 1200
Disposer | 950 | VA | 1 | ea | 950 | 100% | 950
Dishwasher | 1200 | VA | 1 | ea | 1200 | 100% | 1200
TBD | 0 | VA | 0 | ea | 0 | 100% | 0
TBD | 0 | VA | 0 | ea | 0 | 100% | 0
Water Heater | 4500 | VA | 2 | ea | 9000 | 100% | 9000
[6 empty] | Total VA Without Heat | 41550
Mechanical | 15500 | VA/FT^2 | 1 | ft^2 | 15500 | 100% | 15500
Service Totals:
[6 empty] | First 10KVA @100% | 10000
[6 empty] | Remaining @ 40% | 12620
[6 empty] | HVAC @ 100% | 15500
[6 empty] | Total Demand | 38120
[6 empty] | Amps @ 240V, 1P | 158.8333
[6 empty] | Area Ft2 | 3500
[6 empty] | VA/FT^2 | 10.8914

## Multi-Dwelling Service
Optional Service Calculation For Multi-Dwelling Units - Service #1
[8 empty] | # of Units | Demand Factor
Total Units | 19 |  |  | Demand Notes |  | 38% |  | 3-5 | 45
A | 2 | 1500 | 3000 |  |  |  |  | 6-7 | 44
B | 0 | 1500 | 0 |  |  |  |  | 8-10 | 43
C | 4 | 1500 | 6000 |  |  |  |  | 11 | 42
D | 2 | 1500 | 3000 |  |  |  |  | 12-13 | 41
E | 2 | 1500 | 3000 |  |  |  |  | 14-15 | 40
F | 3 | 1500 | 4500 |  |  |  |  | 16-17 | 39
G | 3 | 1500 | 4500 |  |  |  |  | 18-20 | 38
H | 3 | 1500 | 4500 |  |  |  |  | 21 | 37
I | 0 | 1500 | 0 |  |  |  |  | 22-23 | 36
J | 0 | 1500 | 0 |  |  |  |  | 24-25 | 35
K | 0 | 1500 | 0 |  |  |  |  | 26-27 | 34
L | 0 | 1500 | 0 |  |  |  |  | 28-30 | 33
M | 0 | 1500 | 0 |  |  |  |  | 31 | 32
N | 0 | 1500 | 0 |  |  |  |  | 32-33 | 31
[8 empty] | 34-36 | 30
Total Ft2 |  |  | 28500 |  |  |  |  | 37-38 | 29
| Load | Units | Mult | Units | Ext | DF | Total
Lighting | 3 | VA/FT^2 | 28500 | ft^2 | 85500 | 38% | 32490
Small Appliance BC | 1500 | VA | 38 | ea | 57000 | 38% | 21660
Laundry BC | 1500 | VA | 19 | ea | 28500 | 38% | 10830
Range | 9100 | VA | 19 | ea | 172900 | 38% | 65702
Washer / Dryer | 5000 | VA | 19 | ea | 95000 | 38% | 36100
Microwave | 1000 | VA | 19 | ea | 19000 | 38% | 7220
Refrigerator | 1200 | VA | 19 | ea | 22800 | 38% | 8664
Disposer | 960 | VA | 19 | ea | 18240 | 38% | 6931.2
Dishwasher | 1200 | VA | 19 | ea | 22800 | 38% | 8664
Water Heater | 4500 | VA | 19 | ea | 85500 | 38% | 32490
Mechanical 3-phase | 8 | VA/FT^2 | 28500 | ft^2 | 228000 | 38% | 86640
Service Totals: | [5 empty] | Total VA | 317391.2
[6 empty] | Amps @ 208V, 3P | 880.9081
[6 empty] | Area Ft2 | 28500
[6 empty] | VA/FT^2 | 11.1365
Equipment Size | Device | Mult | Width | Total | Depth
| 1200A Main Section | 1 | 32 | 32 | 18
| 200A (3) Meter Center | 0 | 20 | 0 | 10
|  |  | Total | 2.6667 | Ft.

## Pad Mount Trans. Isc
Three-Phase Pad Mount Transformer Isc
kVA (Transformer) | 150
Vll | 208
Ifl =(kVA*1000)/(Vll*1.732) | 416.3706
Transformer % Impedance | 2.4
Multiplier =100/% Impedance | 41.6667
Isc =(Ifl*Multiplier) | 17348.7742
Single-Phase Pad Mount Transformer Isc
kVA (Transformer) | 100
Vll | 240
Ifl =(kVA*1000)/Vll | 416.6667
Transformer % Impedance | 2
Multiplier =100/% Impedance | 50
Isc =(Ifl*Multiplier) | 20833.3333

## Line Current
Line Current Calculator - 3 phase delta loads
| Lgt #1 | Ltg #2
Ballast VA | 1000 | 0
Ballast Voltage | 480 | 480
# Fixtures | 30 | 0
A-B | 10 | 0
B-C | 10 | 0
C-A | 10 | 0
Phase Current |  | Angle | x | y
A-B | 20.8333 | 30 | 18.0422 | 10.4167
B-C | 20.8333 | 270 | -3.8286e-15 | -20.8333
C-A | 20.8333 | 150 | -18.0422 | 10.4167
Line Current |  | Angle | x | y
Aa | 36.0844 | 0 | 36.0844 | 0
Bb | 36.0844 | -120 | -18.0422 | -31.25
Cc | 36.0844 | -240 | -18.0422 | 31.25
Cont. Line Current
Aa | 45.1055
Bb | 45.1055
Cc | 45.1055

## Fire Pump Generator
Fire Pump Calculator
Motor HP | 60
Motor FLC | 169 | Min. Amp. | 211.25
Voltage | 208
Distance to Generator | 100
Locked-Rotor Current | 1200 | Solid State Controller
K | 12.9
Fire Pump Controller Calculation |  |  | Voltage Drop
Allowed 15% VD to Controller | 31.2 |  | Cmil Selected | 500000
Cmil | 85933.8462 |  | Voltage Drop | 5.3623
|  |  | % Voltage Drop | 2.578
Motor Terminal Calculation |  |  | Voltage Drop
Allowed 5% VD to Motor Terminals | 10.4 |  | Cmil Selected | 500000
Cmil @ 115% FLC | 41753.1075 |  | Voltage Drop | 0.86846
|  |  | % Voltage Drop | 0.41753
Electric Fire Pump Controllers | % Starting Current | Table 430.250 - Full Load Current - 3P |  |  | Table 430.251(B) - Maximum Locked Rotor Current
Full Voltage | Table 430.251 (B) | HP | 208V | 460V | HP | 208V | 460V
Part Winding | 390 | 10 | 30.8 | 14 | 10 | 179 | 81 |  |  |  | Ampac.
Wye-Delta Open Transition | 200 | 15 | 46.2 | 21 | 15 | 257 | 116 | Circular Mils |  | K | 60/75 C
Wye-Delta Closed Transition | 200 | 20 | 59.4 | 27 | 20 | 321 | 145 | #3 | 52620 | 12.89 | 85
Primary Resistance | 300 | 25 | 74.8 | 34 | 25 | 404 | 183 | #2 | 66360 | 12.87 | 95
Auto-Transformer 50%, 65%, 80% Taps | 150, 252, 384 | 30 | 88 | 40 | 30 | 481 | 218 | #1 | 83690 | 12.88 | 110
Solid State | 240 | 40 | 114 | 52 | 40 | 641 | 290 | #1/0 | 105600 | 12.88 | 150
|  | 50 | 143 | 65 | 50 | 802 | 363 | #2/0 | 133100 | 12.87 | 175
|  | 60 | 169 | 77 | 60 | 962 | 435 | #3/0 | 167800 | 12.85 | 200
|  | 75 | 211 | 96 | 75 | 1200 | 543 | #4/0 | 211600 | 12.86 | 230
|  | 100 | 273 | 124 | 100 | 1603 | 725 | 250 kcmil | 250000 | 12.88 | 255
|  | 125 | 343 | 156 | 125 | 2007 | 908 | 350 kcmil | 350000 | 12.9 | 310
|  | 150 | 396 | 180 | 150 | 2400 | 1085 | 500 kcmil | 500000 | 12.9 | 380
|  | 200 | 528 | 240 | 200 | 3207 | 1450

## Fire Pump Transformer
Fire Pump Calculator
Motor HP | 75
Motor FLC | 211 | Min. Amp. | 263.75
Voltage | 208
Distance to Transformer | 200
Locked-Rotor Current | 1200 | Solid State Controller
K | 12.9
Fire Pump Controller Calculation |  |  | Voltage Drop
Allowed 15% VD to Controller | 31.2 |  | Cmil Selected | 500000
Cmil | 171867.6923 |  | Voltage Drop | 10.7245
|  |  | % Voltage Drop | 5.156
Motor Terminal Calculation |  |  | Voltage Drop
Allowed 5% VD to Motor Terminals | 10.4 |  | Cmil Selected | 500000
Cmil @ 115% FLC | 104259.2388 |  | Voltage Drop | 2.1686
|  |  | % Voltage Drop | 1.0426
Electric Fire Pump Controllers | % Starting Current | Table 430.250 - Full Load Current - 3P |  |  | Table 430.251(B) - Maximum Locked Rotor Current
Full Voltage | Table 430.251 (B) | HP | 208V | 460V | HP | 208V | 460V
Part Winding | 390 | 10 | 30.8 | 14 | 10 | 179 | 81 |  |  |  | Ampac.
Wye-Delta Open Transition | 200 | 15 | 46.2 | 21 | 15 | 257 | 116 | Circular Mils |  | K | 60/75 C
Wye-Delta Closed Transition | 200 | 20 | 59.4 | 27 | 20 | 321 | 145 | #3 | 52620 | 12.89 | 85
Primary Resistance | 300 | 25 | 74.8 | 34 | 25 | 404 | 183 | #2 | 66360 | 12.87 | 95
Auto-Transformer 50%, 65%, 80% Taps | 150, 252, 384 | 30 | 88 | 40 | 30 | 481 | 218 | #1 | 83690 | 12.88 | 110
Solid State | 240 | 40 | 114 | 52 | 40 | 641 | 290 | #1/0 | 105600 | 12.88 | 150
|  | 50 | 143 | 65 | 50 | 802 | 363 | #2/0 | 133100 | 12.87 | 175
|  | 60 | 169 | 77 | 60 | 962 | 435 | #3/0 | 167800 | 12.85 | 200
|  | 75 | 211 | 96 | 75 | 1200 | 543 | #4/0 | 211600 | 12.86 | 230
|  | 100 | 273 | 124 | 100 | 1603 | 725 | 250 kcmil | 250000 | 12.88 | 255
|  | 125 | 343 | 156 | 125 | 2007 | 908 | 350 kcmil | 350000 | 12.9 | 310
|  | 150 | 396 | 180 | 150 | 2400 | 1085 | 500 kcmil | 500000 | 12.9 | 380
|  | 200 | 528 | 240 | 200 | 3207 | 1450